## Restraint Calculator
|  | = | Input Value
|  | = | Auto Updated Value
Thrust Block Sizing
| Design Pressure (psi) |  |  | 60 |  | Design Pressure = Operating Pressure + 100 psi Surge Allowance
| Soil Type |  |  | Silt
| Soil Bearing Capacity (psf) |  |  | 1500
| Safety Factor |  |  | 1.5
| Horizontal Thrust Blocks | [7 empty] | Gravity Thrust Blocks
| Type Fitting |  | Bearing Area (square feet) | [5 empty] | Type Fitting |  | Volume of Concrete (cubic yards)
|  |  | 6" | 8" | 10" | 12" | 16" |  |  |  | 6" | 8" | 10" | 12" | 16"
90 | Tee or Dead End |  | 3.165 | 5.456 | 8.2053 | 11.6079 | 20.1695 |  | 90˚ Bend |  | 0.82889 | 1.4289 | 2.1489 | 3.04 | 5.2822
90 | 90˚ Bend |  | 3.165 | 5.456 | 8.2053 | 11.6079 | 20.1695 |  | 45˚ Bend |  | 0.58611 | 1.0104 | 1.5195 | 2.1496 | 3.7351
45 | 45˚ Bend |  | 1.7129 | 2.9528 | 4.4407 | 6.2821 | 10.9157 |  | 22.5˚ Bend |  | 0.3172 | 0.54681 | 0.82234 | 1.1634 | 2.0214
22.5 | 22.5˚ Bend |  | 0.87322 | 1.5053 | 2.2638 | 3.2026 | 5.5648 |  | 11.25˚ Bend |  | 0.16171 | 0.27876 | 0.41923 | 0.59307 | 1.0305
11.25 | 11.25˚ Bend |  | 0.43872 | 0.7563 | 1.1374 | 1.609 | 2.7958
Restrained Joint Lengths
Design Pressure = Operating Pressure + 100 psi Surge Allowance
| Design Pressure (psi) |  |  | 60
Soil Description
| Depth to T.O.P. (ft) |  |  | 3 |  |  | Sand or Gravel With Silt
[7 empty] | Φ (deg) | fΦ | Cs (psf) | fc | γ (pcf) | Kn
| Soil Type |  |  | Sand/Silt |  |  | 30 | 0.75 | 0 | 0 | 90 | 0.85
| Trench Type |  |  | 4 |  |  | Trench Description
Pipe bedded in sand, gravel, or crushed stone to a depth of 1/8 pipe diameter, 4 inch min. Backfill compacted to top of pipe.
| Safety Factor |  |  | 1.5
Bends (Horizontal & Vertical)
| No Polyethylene Encasement | [7 empty] | Polyethylene Encasement
| Type Fitting |  | Min. Restrained Joint Lengths (ft) Both Sides of Fitting | [5 empty] | Type Fitting |  | Min. Restrained Joint Lengths (ft) Both Sides of Fitting
| Bends |  | 6" | 8" | 10" | 12" | 16" |  | Bends |  | 6" | 8" | 10" | 12" | 16"
| Horizontal | [7 empty] | Horizontal
90 | 90˚ Bend |  | 9.2853 | 12.1042 | 14.3721 | 16.8139 | 21.2513 |  | 90˚ Bend |  | 10.5312 | 13.7195 | 16.2729 | 19.0292 | 24.0207
45 | 45˚ Bend |  | 3.8461 | 5.0137 | 5.9531 | 6.9646 | 8.8026 |  | 45˚ Bend |  | 4.3622 | 5.6828 | 6.7405 | 7.8822 | 9.9497
22.5 | 22.5˚ Bend |  | 1.847 | 2.4077 | 2.8588 | 3.3445 | 4.2271 |  | 22.5˚ Bend |  | 2.0948 | 2.729 | 3.2369 | 3.7852 | 4.778
11.25 | 11.25˚ Bend |  | 0.91452 | 1.1922 | 1.4155 | 1.656 | 2.0931 |  | 11.25˚ Bend |  | 1.0372 | 1.3513 | 1.6027 | 1.8742 | 2.3658
| Vertical (Down) | [7 empty] | Vertical (Down)
90 | 90˚ Bend |  | 23.5459 | 30.8412 | 36.913 | 43.3292 | 55.2969 |  | 90˚ Bend |  | 33.6371 | 44.0588 | 52.7329 | 61.8988 | 78.9955
45 | 45˚ Bend |  | 9.7531 | 12.7748 | 15.2899 | 17.9475 | 22.9047 |  | 45˚ Bend |  | 13.9329 | 18.2498 | 21.8427 | 25.6393 | 32.721
22.5 | 22.5˚ Bend |  | 4.6836 | 6.1347 | 7.3425 | 8.6187 | 10.9992 |  | 22.5˚ Bend |  | 6.6908 | 8.7638 | 10.4892 | 12.3124 | 15.7132
11.25 | 11.25˚ Bend |  | 2.3191 | 3.0376 | 3.6356 | 4.2675 | 5.4463 |  | 11.25˚ Bend |  | 3.313 | 4.3394 | 5.1937 | 6.0965 | 7.7804
| Vertical (Up) | [7 empty] | Vertical (Up)
90 | 90˚ Bend |  | 9.2853 | 12.1042 | 14.3721 | 16.8139 | 21.2513 |  | 90˚ Bend |  | 10.5312 | 13.7195 | 16.2729 | 19.0292 | 24.0207
45 | 45˚ Bend |  | 3.8461 | 5.0137 | 5.9531 | 6.9646 | 8.8026 |  | 45˚ Bend |  | 4.3622 | 5.6828 | 6.7405 | 7.8822 | 9.9497
22.5 | 22.5˚ Bend |  | 1.847 | 2.4077 | 2.8588 | 3.3445 | 4.2271 |  | 22.5˚ Bend |  | 2.0948 | 2.729 | 3.2369 | 3.7852 | 4.778
11.25 | 11.25˚ Bend |  | 0.91452 | 1.1922 | 1.4155 | 1.656 | 2.0931 |  | 11.25˚ Bend |  | 1.0372 | 1.3513 | 1.6027 | 1.8742 | 2.3658
| Dead End | [7 empty] | Dead End
|  |  | 23.5459 | 30.8412 | 36.913 | 43.3292 | 55.2969 |  |  |  | 33.6371 | 44.0588 | 52.7329 | 61.8988 | 78.9955
Tees
| No Polyethylene Encasement | [7 empty] | Polyethylene Encasement
| Type Fitting (Tee Run x Branch) |  | Total Length (ft) Between Unrestrained Joints of Tee |  | Restrained Length (ft) of Branch |  |  |  | Type Fitting (Tee Run x Branch) |  | Total Length (ft) Between Unrestrained Joints of Tee |  | Restrained Length (ft) of branch
| 6 x 6 |  | 1 |  | 22.0101 |  |  |  | 6 x 6 |  | 1 |  | 31.443
|  |  | 5 |  | 15.8668 | [5 empty] | 5 |  | 22.6669
|  |  | 10 |  | 8.1877 | [5 empty] | 10 |  | 11.6967
|  |  | 15 |  | 0.50859 | [5 empty] | 15 |  | 0.72656
|  |  | 20 |  | -7.1705 | [5 empty] | 20 |  | -10.2436
| 8 x 6 |  | 1 |  | 16.3428 |  |  |  | 8 x 6 |  | 1 |  | 23.3468
|  |  | 5 |  | 10.1509 | [5 empty] | 5 |  | 14.5012
|  |  | 10 |  | 2.411 | [5 empty] | 10 |  | 3.4442
|  |  | 15 |  | -5.3289 | [5 empty] | 15 |  | -7.6128
|  |  | 20 |  | -13.0688 | [5 empty] | 20 |  | -18.6698
| 8 x 8 |  | 1 |  | 29.2932 |  |  |  | 8 x 8 |  | 1 |  | 41.8474
|  |  | 5 |  | 23.1013 | [5 empty] | 5 |  | 33.0018
|  |  | 10 |  | 15.3614 | [5 empty] | 10 |  | 21.9448
|  |  | 15 |  | 7.6215 | [5 empty] | 15 |  | 10.8878
|  |  | 20 |  | -0.11841 | [5 empty] | 20 |  | -0.16916
| 10 x 8 |  | 1 |  | 22.9767 |  |  |  | 10 x 8 |  | 1 |  | 32.8239
|  |  | 5 |  | 16.7032 | [5 empty] | 5 |  | 23.8617
|  |  | 10 |  | 8.8613 | [5 empty] | 10 |  | 12.659
|  |  | 15 |  | 1.0195 | [5 empty] | 15 |  | 1.4564
|  |  | 20 |  | -6.8224 | [5 empty] | 20 |  | -9.7463
| 10 x 10 |  | 1 |  | 35.3447 |  |  |  | 10 x 10 |  | 1 |  | 50.4924
|  |  | 5 |  | 29.0712 | [5 empty] | 5 |  | 41.5302
|  |  | 10 |  | 21.2293 | [5 empty] | 10 |  | 30.3276
|  |  | 15 |  | 13.3874 | [5 empty] | 15 |  | 19.1249
|  |  | 20 |  | 5.5456 | [5 empty] | 20 |  | 7.9222
| 12 x 10 |  | 1 |  | 27.4742 |  |  |  | 12 x 10 |  | 1 |  | 39.2488
|  |  | 5 |  | 14.8584 | [5 empty] | 5 |  | 21.2262
|  |  | 10 |  | -0.9114 | [5 empty] | 10 |  | -1.302
|  |  | 15 |  | -16.6812 | [5 empty] | 15 |  | -23.8302
|  |  | 20 |  | -0.9114 | [5 empty] | 20 |  | -46.3585
| 12 x 12 |  | 1 |  | 40.1752 |  |  |  | 12 x 12 |  | 1 |  | 57.3931
|  |  | 5 |  | 27.5594 | [5 empty] | 5 |  | 39.3705
|  |  | 10 |  | 11.7896 | [5 empty] | 10 |  | 16.8423
|  |  | 15 |  | -3.9802 | [5 empty] | 15 |  | -5.6859
|  |  | 20 |  | -19.7499 | [5 empty] | 20 |  | -28.2142
| 16 x 12 |  | 1 |  | 30.2221 |  |  |  | 16 x 12 |  | 1 |  | 43.1745
|  |  | 5 |  | 23.8139 | [5 empty] | 5 |  | 34.0199
|  |  | 10 |  | 15.8037 | [5 empty] | 10 |  | 22.5767
|  |  | 15 |  | 7.7935 | [5 empty] | 15 |  | 11.1335
|  |  | 20 |  | -0.21678 | [5 empty] | 20 |  | -0.30969
| 16 x 16 |  | 1 |  | 53.6948 |  |  |  | 16 x 16 |  | 1 |  | 76.7069
|  |  | 5 |  | 47.2866 | [5 empty] | 5 |  | 67.5523
|  |  | 10 |  | 39.2764 | [5 empty] | 10 |  | 56.1091
|  |  | 15 |  | 31.2661 | [5 empty] | 15 |  | 44.6659
|  |  | 20 |  | 23.2559 | [5 empty] | 20 |  | 33.2227
| Joint Restraint (Bends) | [6 empty] | Joint Restraint (Tees)
Horizontal - Bends
| Fs = Ff | 142.5723 | 187.6387 | 235.7704 | 284.1505 | 386.8755 |  | Rs = KnPpD'r
| Fs = Ff (Polyethylene Encasement) | 99.8006 | 131.3471 | 165.0393 | 198.9054 | 270.8128 |  | Rs | 437.9319 | 580.9219 | 580.9219 | 739.5523 | 739.5523 | 896.1975 | 896.1975 | 1239.5869 | 1239.5869
| Pp | 888.3 | 911.25 | 935.55 | 958.5 | 1005.75 |  | Pp | 888.3 | 911.25 | 911.25 | 935.55 | 935.55 | 958.5 | 958.5 | 1005.75 | 1005.75
| Rs | 437.9319 | 580.9219 | 739.5523 | 896.1975 | 1239.5869 |  | (Fs)b | 142.5723 | 142.5723 | 187.6387 | 187.6387 | 235.7704 | 235.7704 | 284.1505 | 284.1505 | 386.8755
[8 empty] | D'r | 0.58 | 0.75 | 0.75 | 0.93 | 0.93 | 1.1 | 1.1 | 1.45 | 1.45
| Vertical (Down) | [6 empty] | Ab (in^2) | 37.3 | 37.3 | 64.3 | 64.3 | 96.7 | 96.7 | 136.8 | 136.8 | 237.7
| Fs = Ff | 142.5723 | 187.6387 | 235.7704 | 284.1505 | 386.8755 |  | Run x Branch | 6 x 6 | 8 x 6 | 8 x 8 | 10 x 8 | 10 x 10 | 12 x 10 | 12 x 12 | 16 x 12 | 16 x 16
| Fs = Ff (Polyethylene Encasement) | 99.8006 | 131.3471 | 165.0393 | 198.9054 | 270.8128
| Pp | 888.3 | 911.25 | 935.55 | 958.5 | 1005.75 |  | L = | SfPAb - 1/2RsLr
Ff
Vertical (Up)
| Fs = Ff | 142.5723 | 187.6387 | 235.7704 | 284.1505 | 386.8755 |  | Tees | 6" Run | 8" Run | 10" Run | 12" Run | 16" Run
| Fs = Ff (Polyethylene Encasement) | 99.8006 | 131.3471 | 165.0393 | 198.9054 | 270.8128 |  | Fs = Ff | 142.5723 | 187.6387 | 235.7704 | 284.1505 | 386.8755
| Pp | 888.3 | 911.25 | 935.55 | 958.5 | 1005.75 |  | Fs = Ff (Polyethylene Encasement) | 99.8006 | 131.3471 | 165.0393 | 198.9054 | 270.8128
| Rs | 437.9319 | 580.9219 | 739.5523 | 896.1975 | 1239.5869
Dead End
| Fs = Ff | 142.5723 | 187.6387 | 235.7704 | 284.1505 | 386.8755
| Fs = Ff (Polyethylene Encasement) | 99.8006 | 131.3471 | 165.0393 | 198.9054 | 270.8128
|  | 6" | 8" | 10" | 12" | 16"
| W | 344.2 | 453 | 569.2 | 686 | 934
| We | 156.6 | 202.5 | 251.1 | 297 | 391.5 |  | Wm (concrete) = |  | 150
| Wp | 18 | 24 | 30 | 39 | 57
| Ww | 13 | 24 | 37 | 53 | 94
| H | 3 | 3 | 3 | 3 | 3 |  | Soil Parameters
| Hc | 3.29 | 3.375 | 3.465 | 3.55 | 3.725
| D' | 0.58 | 0.75 | 0.93 | 1.1 | 1.45 |  | Soil | Soil Description |  |  |  |  | Φ (deg) | fΦ | Cs (psf) | fc | γ (pcf)
| C | 0 | 0 | 0 | 0 | 0 |  | Clay 1 | Clay of Medium to Low Plasticity, LL<50 |  |  |  |  | 0 | 0 | 300 | 0.8 | 90
| tan(δ) | 0.41421 | 0.41421 | 0.41421 | 0.41421 | 0.41421 |  | Silt 1 | Silt of Medium to Low Plasticity, LL<50 |  |  |  |  | 29 | 0.75 | 0 | 0 | 90
| δ | 22.5 | 22.5 | 22.5 | 22.5 | 22.5 |  | Clay 2 | Clay of Medium to Low Plasticity w/Sand or Gravel |  |  |  |  | 0 | 0 | 300 | 0.8 | 90
| NΦ | 3 | 3 | 3 | 3 | 3 |  | Silt 2 | Silt of Medium to Low Plasticity w/Sand or Gravel |  |  |  |  | 29 | 0.75 | 0 | 0 | 90
| SQRT NΦ | 1.7321 | 1.7321 | 1.7321 | 1.7321 | 1.7321 |  | Coh-Gran | Cohesive Granular Soils |  |  |  |  | 20 | 0.65 | 200 | 0.4 | 90
| Φ (deg) | 30 | 30 | 30 | 30 | 30 |  | Sand/Silt | Sand or Gravel w/Silt |  |  |  |  | 30 | 0.75 | 0 | 0 | 90
| fΦ | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 |  | Good Sand/Gravel | Clean Sand or Gravel |  |  |  |  | 36 | 0.8 | 0 | 0 | 100
| Cs (psf) | 0 | 0 | 0 | 0 | 0
| fc | 0 | 0 | 0 | 0 | 0
| γ (pcf) | 90 | 90 | 90 | 90 | 90
| Kn | 0.85 | 0.85 | 0.85 | 0.85 | 0.85
| Area (in^2) | 37.3 | 64.3 | 96.7 | 136.8 | 237.7
| Ap (bends) | 0.9106 | 1.1775 | 1.4601 | 1.727 | 2.2765
| Ap (Tee) | 1.8212 | 2.355 | 2.9202 | 3.454 | 4.553
Bends - Horizontal
Restrained Length (ft) = |  |  | SfPA tan(Θ/2)
Ff + 1/2(Rs)
Bends - Vertical (Down)
Restrained Length (ft) = |  |  | SfPA tan(Θ/2)
Ff
Bends - Vertical (Up)
Restrained Length (ft) = |  |  | SfPA tan(Θ/2)
Ff + 1/2(Rs)
Dead Ends
Restrained Length (ft) = |  |  | SfPA
Ff
Note on E8: kaneap: Input Working Pressure
Note on E14: kaneap: Input Safety Factor
Note on E29: kaneap: Input Working Pressure
Note on E31: kaneap: Input Depth to Top Of Pipe
Note on E35: kaneap: Select Trench Type (refer to "Trench Type" tab for more information)
Note on E37: kaneap: Input Safety Factor

## Soil Characteristics
Horizontal Bearing Strengths
Soil | Bearing Strength(psf)
Muck | 0
Soft Clay | 1000
Silt | 1500
Sandy Silt | 3000
Sand | 4000
Sandy Clay | 6000
Hard Clay | 9000
Soil Parameters | [6 empty] | Kn
Trench Type
Soil | Soil Description | Φ (deg) | fΦ | Cs (psf) | fc | γ (pcf) | 2 | 3 | 4 | 5
Clay 1 | Clay of Medium to Low Plasticity, LL<50 | 0 | 0 | 300 | 0.8 | 90 | 0.2 | 0.4 | 0.6 | 0.85
Silt 1 | Silt of Medium to Low Plasticity, LL<50 | 29 | 0.75 | 0 | 0 | 90 | 0.2 | 0.4 | 0.6 | 0.85
Clay 2 | Clay of Medium to Low Plasticity w/Sand or Gravel | 0 | 0 | 300 | 0.8 | 90 | 0.4 | 0.6 | 0.85 | 1
Silt 2 | Silt of Medium to Low Plasticity w/Sand or Gravel | 29 | 0.75 | 0 | 0 | 90 | 0.4 | 0.6 | 0.85 | 1
Coh-Gran | Cohesive Granular Soils | 20 | 0.65 | 200 | 0.4 | 90 | 0.4 | 0.6 | 0.85 | 1
Sand/Silt | Sand or Gravel w/Silt | 30 | 0.75 | 0 | 0 | 90 | 0.4 | 0.6 | 0.85 | 1
Good Sand/Gravel | Clean Sand or Gravel | 36 | 0.8 | 0 | 0 | 100 | 0.4 | 0.6 | 0.85 | 1

## Thrust Block-Trench Type
Trench Type
Trench Type 2 | Trench Type 3 | Trench Type 4 | Trench Type 5
Flat-bottom trench. Backfill lightly consolidated to centerline of pipe. | Pipe bedded in 4 inches minimum loose soil. Backfill lightly consolidated to top of the pipe. | Pipe bedded in sand, gravel, or crushed stone to a depth of 1/8 pipe diameter, 4 inch minimum. Backfill compacted to top of pipe. | Pipe bedded in compacted granular material to the centerline of the pipe, 4 inches minimum under the pipe. Compacted granular or select material to top of pipe.
Thrust Blocks
*Bearing Area = L x L
L
L
L
L

## Guidance
Engineering has developed an Excel Calculator (Rows 27 - 64) that will let you know if there is enough buried straight pipe on the downstream side of a valve that will resist the upstream pressure when the valve is closed. Use the "Deadend" Fitting Type for the closed valve situation. It will give you an answer when you enter the following parameters:
diameter of main
length of piping that will provide restraint
highest operating pressure on the pressure side of the valve
depth of bury
safety factor
The tool uses a conservative soil designation which also provides some additional safety factor. No need to analyze the soil type. It also uses a Class 4 Trench Type since it has been compacted over time. I recommend always using a 1.5 safety factor due to any unknown or length or depth error measurement(s). The only other parameter that needs to be field estimated is the Surge Allowance. If the piping location is not near a WTP, Booster Station, or PRV Station, my advice is to use "0" Surge Pressure as long as we perform the hydrant replacement within 4-6 hours. The longer the time, the more chance for a surge wave to push against the valve. If we are close to a Station, we should add at least 50 psi to the operating psi since the probability of experiencing a power outage during the hydrant replacement is low.